## unit 1
AC-DC Single Output Voltage external Power Supply Test Report
Lab Test Results |  |  |  |  | Limits
Manufacturer Name |  | Globtek,Inc. |  |  | CEC Level IV |  | Energy Star Level V
Model |  | GT-41052-1305 |  |  | Ave. Efficiency | No Load power | Ave. Efficiency | No Load power
Part number: |  | WR9QA2600CCP-N |  |  | 73.08% | 0.5 W | 75.34% | 0.3 W
Nameplate Specifications
Related Product Specifications |  |  | Input | Output
Voltage (V) |  |  | 100-240 | 5
Current (A) |  |  | 0.6 | 2.6
Power (Watts) |  |  |  | 13
Frequency (Hz) |  |  | 50-60
Date Measured | 2006-06-01 |  | NOV 29 2011
Ambient Temp. °C | (25+/-5)°C |  | 25 Deg C
Output Cord AWG and Length |  |  | 18AWM,1830(+/-10)mm
Type of Output Cord |  |  | 1185, VW-1, E330069, SUHUA, FT1
|  |  | Active Power Measurements |  |  |  | No Load
Percent of Rated Load |  |  | 100% | 75% | 50% | 25% | 0% | Average
DC Output Current (mA) |  |  | 2600 | 1950 | 1300 | 650 | 0
DC Output Voltage (V) |  |  | 4.79 | 4.89 | 4.99 | 5.09 | 5.2
DC Output Power (W) |  |  | 12.454 | 9.5355 | 6.487 | 3.3085 | 0
AC Input Voltage (V) |  |  | 115
AC Input Power (W) |  |  | 17.573 | 12.964 | 8.5459 | 4.3414 | 0.0887
Total Harmonic Distortion (THD) |  |  | 0.1828 | 0.1636 | 0.1415 | 0.119 | 0.092 | 0.13978
True Power Factor(Watts/VA) |  |  | 0.5672 | 0.5376 | 0.4951 | 0.4268 | 0.0383 | 0.413
Ac Input Frequency |  |  | 60 | 60 | 60 | 60 | 60 | 60
Power Consumed by UUT (W) |  |  | 5.119 | 3.4285 | 2.0589 | 1.0329
Efficiency |  |  | 70.87% | 73.55% | 75.91% | 76.21% |  | 74.13%
|  |  | Active Power Measurements |  |  |  | No Load
Percent of Rated Load |  |  | 100% | 75% | 50% | 25% | 0% | Average
DC Output Current (mA) |  |  | 2600 | 1950 | 1300 | 650 | 0
DC Output Voltage (V) |  |  | 4.79 | 4.89 | 4.98 | 5.1 | 5.19
DC Output Power (W) |  |  | 12.454 | 9.5355 | 6.474 | 3.315 | 0
AC Input Voltage (V) |  |  | 230
AC Input Power (W) |  |  | 17.65 | 13.078 | 8.8605 | 4.5125 | 0.1371
Total Harmonic Distortion (THD) |  |  | 0.0909 | 0.0817 | 0.0737 | 0.0662 | 0.0526 | 0.07302
True Power Factor(Watts/VA) |  |  | 0.4315 | 0.4073 | 0.3741 | 0.3114 | 0.0209 | 0.30904
Ac Input Frequency |  |  | 50 | 50 | 50 | 50 | 50 | 50
Power Consumed by UUT (W) |  |  | 5.196 | 3.5425 | 2.3865 | 1.1975
Efficiency |  |  | 70.56% | 72.91% | 73.07% | 73.46% |  | 72.5%

## unit 2
AC-DC Single Output Voltage external Power Supply Test Report
Lab Test Results |  |  |  |  | Limits
Manufacturer Name |  | Globtek,Inc. |  |  | CEC level IV |  | Energy Star Level V
Model |  | GT-41052-1305 |  |  | Ave. Efficiency | No Load power | Ave. Efficiency | No Load power
Part number: |  | WR9QA2600CCP-N |  |  | 73.08% | 0.5 W | 75.34% | 0.3 W
Nameplate Specifications
Related Product Specifications |  |  | Input | Output
Voltage (V) |  |  | 100-240 | 5
Current (A) |  |  | 0.6 | 2.6
Power (Watts) |  |  |  | 13
Frequency (Hz) |  |  | 50-60
Date Measured |  |  | 2011-11-28
Ambient Temp. °C | (25+/-5)°C |  | 25 Deg
Output Cord AWG and Length |  |  | 18AWM,1830(+/-10)mm
Type of Output Cord |  |  | 1185, VW-1, E330069, SUHUA, FT1
|  |  | Active Power Measurements |  |  |  | No Load
Percent of Rated Load |  |  | 100% | 75% | 50% | 25% | 0% | Average
DC Output Current (mA) |  |  | 2600 | 1950 | 1300 | 650 | 0
DC Output Voltage (V) |  |  | 4.82 | 4.9 | 5 | 5.1 | 5.2
DC Output Power (W) |  |  | 12.532 | 9.555 | 6.5 | 3.315 | 0
AC Input Voltage (V) |  |  | 115
AC Input Power (W) |  |  | 17.505 | 12.924 | 8.5454 | 4.3876 | 0.0864
Total Harmonic Distortion (THD) |  |  | 0.1809 | 0.1644 | 0.1446 | 0.1203 | 0.0923 | 0.1405
True Power Factor(Watts/VA) |  |  | 0.5694 | 0.5389 | 0.4961 | 0.4282 | 0.0382 | 0.41416
Ac Input Frequency |  |  | 60 | 60 | 60 | 60 | 60 | 60
Power Consumed by UUT (W) |  |  | 4.973 | 3.369 | 2.0454 | 1.0726
Efficiency |  |  | 71.59% | 73.93% | 76.06% | 75.55% |  | 74.29%
|  |  | Active Power Measurements |  |  |  | No Load
Percent of Rated Load |  |  | 100% | 75% | 50% | 25% | 0% | Average
DC Output Current (mA) |  |  | 2600 | 1950 | 1300 | 650 | 0
DC Output Voltage (V) |  |  | 4.82 | 4.91 | 5 | 5.1 | 5.2
DC Output Power (W) |  |  | 12.532 | 9.5745 | 6.5 | 3.315 | 0
AC Input Voltage (V) |  |  | 230
AC Input Power (W) |  |  | 17.903 | 13.241 | 8.935 | 4.544 | 0.1432
Total Harmonic Distortion (THD) |  |  | 0.0915 | 0.0844 | 0.0768 | 0.0638 | 0.0527 | 0.07384
True Power Factor(Watts/VA) |  |  | 0.4328 | 0.4065 | 0.3719 | 0.3083 | 0.0208 | 0.30806
Ac Input Frequency |  |  | 50 | 50 | 50 | 50 | 50 | 50
Power Consumed by UUT (W) |  |  | 5.371 | 3.6665 | 2.435 | 1.229
Efficiency |  |  | 71.59% | 74.08% | 76.06% | 75.55% |  | 74.32%

## unit 3
AC-DC Single Output Voltage external Power Supply Test Report
Lab Test Results |  |  |  |  | Limits
Manufacturer Name |  | Globtek,Inc. |  |  | CEC IV |  | Energy Star Level V
Model |  | GT-41052-1305 |  |  | Ave. Efficiency | No Load power | Ave. Efficiency | No Load power
Part number: |  | WR9QA2600CCP-N |  |  | 73.08% | 0.5 W | 75.34% | 0.3 W
Nameplate Specifications
Related Product Specifications |  |  | Input | Output
Voltage (V) |  |  | 100-240 | 5
Current (A) |  |  | 0.6 | 2.6
Power (Watts) |  |  |  | 13
Frequency (Hz) |  |  | 50-60
Date Measured |  |  | NOV-28-11
Ambient Temp. °C | (25+/-5)°C |  | 28 Deg
Output Cord AWG and Length |  |  | 18AWM,1830(+/-10)mm
Type of Output Cord |  |  | 1185, VW-1, E330069, SUHUA, FT1
|  |  | Active Power Measurements |  |  |  | No Load
Percent of Rated Load |  |  | 100% | 75% | 50% | 25% | 0% | Average
DC Output Current (mA) |  |  | 2600 | 1950 | 1300 | 650 | 0
DC Output Voltage (V) |  |  | 4.8 | 4.91 | 5.01 | 5.11 | 5.11
DC Output Power (W) |  |  | 12.48 | 9.5745 | 6.513 | 3.3215 | 0
AC Input Voltage (V) |  |  | 115
AC Input Power (W) |  |  | 17.709 | 13.068 | 8.6388 | 4.3539 | 0.0883
Total Harmonic Distortion (THD) |  |  | 0.1842 | 0.1672 | 0.1479 | 0.1204 | 0.0923 | 0.1424
True Power Factor(Watts/VA) |  |  | 0.5707 | 0.5404 | 0.4973 | 0.4277 | 0.0376 | 0.41474
Ac Input Frequency |  |  | 60 | 60 | 60 | 60 | 60 | 60
Power Consumed by UUT (W) |  |  | 5.229 | 3.4935 | 2.1258 | 1.0324
Efficiency |  |  | 70.47% | 73.27% | 75.39% | 76.29% |  | 73.85%
|  |  | Active Power Measurements |  |  |  | No Load
Percent of Rated Load |  |  | 100% | 75% | 50% | 25% | 0% | Average
DC Output Current (mA) |  |  | 2600 | 1950 | 1300 | 650 | 0
DC Output Voltage (V) |  |  | 4.8 | 4.9 | 5.01 | 5.11 | 5.22
DC Output Power (W) |  |  | 12.48 | 9.555 | 6.513 | 3.3215 | 0
AC Input Voltage (V) |  |  | 230
AC Input Power (W) |  |  | 17.679 | 13.081 | 8.9214 | 4.5059 | 0.1412
Total Harmonic Distortion (THD) |  |  | 0.0941 | 0.0865 | 0.0748 | 0.063 | 0.0528 | 0.07424
True Power Factor(Watts/VA) |  |  | 0.4304 | 0.405 | 0.3713 | 0.3088 | 0.0206 | 0.30722
Ac Input Frequency |  |  | 50 | 50 | 50 | 50 | 50 | 50
Power Consumed by UUT (W) |  |  | 5.199 | 3.526 | 2.4084 | 1.1844
Efficiency |  |  | 70.59% | 73.04% | 73% | 73.71% |  | 72.59%